{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Kontorrom","Klasserom","Sheet3"],"not_rendered":{"charts":4,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Kontorrom","index":0,"n_rows":59,"n_cols":48,"rows_kept":59,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
["Inndata"]
["Abra",100,"m2"]
["Afas",102.5,"m2"]
["Avin",20,"m2"]
["Atak",100,"m2"]
["Agulv",100,"m2"]
["Ask.v",31.5,"m2"]
["Takhøyde",2.5,"m"]
["Uvin",1.2,"W/m2K"]
["Uyv",0.18,"W/m2K"]
["Utak",0.13,"W/m2K"]
["Ugulv",0.15,"W/m2K"]
["N50",2.5,"oms/t"]
["V\"",1.2,"m3/hm2"]
["Virkgrad",0.7]
["C\"gulv",41,"Wh/m2K"]
["C\"tak",5,"Wh/m2K"]
["Cvegg",3,"Wh/m2K"]
["Te,sommer",20,"°C"]
["Te,vinter",-20,"°C"]
["Tinne",20,"°C"]
["Ts",20,"°C"]
["q\"lys",4]
["q\"uts",3]
["q\"per",2]
["Solfluks, snitt 08-16",300,"W/m2"]
["g",0.25]
["Fkarm",0.2]
["Fhor",0.8]
["Sommerluftskifte",4,"oms/t"]
["BEREGNINGER"]
["Volum",250,"m3"]
["Htr",66.85,"W/K"]
["Hinf",14.437500000000004,"W/K"]
["Hvent",11.880000000000003,"W/m2K"]
["H",93.16749999999999]
["H\"",0.9316749999999999,"W/m2K"]
["Effektbehov vinter",37.266999999999996,"W/m2"]
["Effektbehov vinter",3726.7,"W"]
["Temp etter gj.vinner",8,"°C"]
["Effektbehov varmebatt",4.896000000000001,"W/m2"]
["Effektbehov rom",32.370999999999995,"W/m2"]
[]
["Dynamiske beregninger"]
["C\"",49.42,"Wh/m2K"]
["H\"",4.0685,"W/Km2"]
["Tau",12.146982917537176,"h"]
["To",20,"°C"]
["Hv",0.396,"W/Km2",39.6]
["q\"int",9,"W/m2"]
["q\"sol",9.6,"W/m2"]
["q\"",18.6,"W/m2"]
["Tuend",35.386206183435014,"°C"]
["t",3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49]
["Ti ",20,20,20,20,20,20,21.215931533388776,22.335771185760063,23.367112846526158,24.31695027992962,25.191724551361958,25.997367705704693,26.73934299388567,27.422681920436077,28.052018363276154,28.631619997103744,29.16541723347477,29.657029873825103,30.109791656173932,30.526772861965565,30.910801136351765,31.264480663101804,31.590209824169598,31.8901974636716,32.16647786656514,32.420924553601076,32.65526298609754,32.871082266688695,33.06984591539403,33.2529017940831,33.421491246635895,33.57675751678025,33.71975350068969,33.851448886913744,33.9727367320583,34.084439516807215,34.187314723352365,34.28205997205406,34.36931775216461,34.449679778695305,34.52369100497149,34.59185331808603,34.654628942310765,34.712443573545215,34.76568926605812,34.81472709109728,34.859889585396495]
[{"$nulls":6},35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014,35.386206183435014]
["Ti (14.00)"," ",{"$nulls":4},0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41]
["Ti (17.00)"," "]

{"sheet":"Klasserom","index":1,"n_rows":52,"n_cols":48,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
["Inndata"]
["Abra",60,"m2"]
["Afas",30,"m2"]
["Avin",16,"m2"]
["Ask.v",66,"m2"]
["Takhøyde",3,"m"]
["Uvin",1.2,"W/m2K"]
["Uyv",0.18,"W/m2K"]
["N50",1.5,"oms/t"]
["V\"",14,"m3/hm2"]
["Virkgrad",0.7]
["C\"gulv",10,"Wh/m2K"]
["C\"tak",63,"Wh/m2K"]
["Cvegg",3,"Wh/m2K"]
["Te,sommer",20,"°C"]
["Te,vinter",-20,"°C"]
["Tinne",20,"°C"]
["Ts",18,"°C"]
["q\"lys",8]
["q\"uts",2]
["q\"per",30]
["Solfluks, snitt 08-16",300,"W/m2"]
["g",0.25]
["Fkarm",0.2]
["Fhor",0.8]
["BEREGNINGER"]
["Volum",180,"m3"]
["Htr",21.72,"W/K"]
["Hinf",6.237000000000001,"W/K"]
["Hvent",83.16000000000001,"W/m2K"]
["H",111.11700000000002]
["H\"",1.8519500000000002,"W/m2K"]
["Effektbehov vinter",74.078,"W/m2"]
["Temp etter gj.vinner",8,"°C"]
["Effektbehov varmebatt",46.2,"W/m2"]
["Effektbehov rom",27.878,"W/m2"]
[]
["Dynamiske beregninger"]
["C\"",77,"Wh/m2K"]
["Tau",15.139747736411092,"h"]
["To",20,"°C"]
["Hv",4.62,"W/Km2",277.2]
["q\"int",40,"W/m2"]
["q\"sol",12.8,"W/m2"]
["q\"",52.8,"W/m2"]
["Tuend",28.56477157659827,"°C"]
["t",3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49]
["Ti ",20,20,20,20,20,20,20.54743584759703,21.05988115229936,21.53957241012281,21.988603166616716,22.408933153851347,22.802396843394984,23.17071145260909,23.51548443920381,23.83822051676283,24.14032822185581,24.42312606139965,24.68784826709795,24.935650182073008,25.167613303199648,25.384750001147392,25.588007938730968,25.778274206852405,25.956379196085475,26.123100220799458,26.279164911639235,26.42525439116768,26.56200624653004,26.690017312114033,26.809846274350257,26.922016110021133,27.027016368720094,27.125305309422455,27.21731190049277,27.30343769185738,27.38405856751303,27.459526386020123,27.530170516140288,27.59629927432038,27.65820127029659,27.71614666669135,27.7703883581004,27.82116307481596,27.86869241600304,27.913183816838092,27.954831453830863,27.99381709228069]
[{"$nulls":6},28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827,28.56477157659827]
["Ti (14.00)"," ",{"$nulls":4},0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41]
["Ti (17.00)"," "]

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}